## Slide 1: Exelon Project update
Lusha Wang, Tianqi hong, zhi zhou, Balasubramaniam, Karthikeyan
Argonne National Laboratory
Sept 6, 2022

## Slide 2: Grid impact update
Co-simulation Environment Setup
Python Environment
OpenDSS
Octave environment
Matpower
Distribution System Analysis
Transmission System Analysis

## Slide 3: Grid impact update
Distribution System Analysis API
  Solve power flow and get operational conditions in the network, including voltages, load and power flow
  Scale load in the system to increase or decrease overall loading condition
  Change substation voltage
  Change controllable status of each load
  Add PVs in the system
  Change DER setpoints
  Change switch status
Transmission System Analysis API
  Run AC power flow and get system operational conditions
  Change load condition in the network

## Slide 4: Grid impact update
Snapshot of Distribution Analysis

## Slide 5: Proposal
Goal
  Develop utility managed smart charging system
  Evaluate smart charging impact on distribution operation
  Evaluate utilities’ ability to control EV charging based on grid conditions
BP 1
  Cybersecurity testing: simulate DR event, develop threat models
  Platform for grid services: test DR, test frequency regulation
  Smart charging management: collect data, develop smart charging measures
  Negotiation and execution with vendors
  NO MILESTONE RELATED

## Slide 6: Proposal
BP 2
  Simulate EV charging demand on grid and evaluate impact
    Develop driver-agent model in ATEAM to determine where and when to charge (Yan Zhou)
    Translate utility-managed smart charging scenarios into ATEAM inputs (Yan Zhou)
    Run simulations in ATEAM for infrastructure and EV adoption evolution under different scenarios (Yan Zhou)
  Install utility-owned charging network
  Collect data and develop system for future economic impact analysis
  Analyze cybersecurity challenges and perform cyber impact analysis
  NO MILESTONE RELATED

## Slide 7: Proposal
BP 3
  Implement smart charge management demonstration
  Re-calibrate ATEAM tool with demo results (Yan Zhou)
  Collect results from ATEAM
  Develop ATEAM-T&D co-simulation tool to analyze grid impact
  Analyze economic impact analysis on EVSEs and the grid
    Evaluate revenue and operational cost of smart charging management and grid service provision profiles
    Assess grid upgrade needs, cost and benefits based on grid and EVSE expansion scenarios
  Perform cyber-physical threat model and impact analysis
  Adjust tactics to improve grid benefit and driver behavior
  MILESTONES:
    Co-simulation tool (ATD) validated
    Impact analysis completed

## Slide 8: Proposal
BP 4
  Conduct second year demonstration of smart charge management demonstration.
  Analyze grid impact
    Perform scenario generation and analysis
    Simulate grid impact, evaluate mitigation options under different scenarios
  Analyze driver behavior and grid benefits
  MILESTONES:
    Data preparation demonstrated
    EV impacts to the grid quantified

## Slide 9: Grid impact analysis update
Done:
  Implementing distribution system operation analysis about randomly adding EV
To Do:
  Testing adding EV function on IEEE 13 node system in co-simulation environment

## Slide 10: Grid impact analysis update
Done:
  Obtained Exelon GIS data for: Maryland, Delaware, New Jersey

## Slide 11: Grid impact analysis update
Done:
  Available Information:
    Secondary transformer location
    Overhead line connection
    Underground cable connection
    Capacitor bank location
    Regulator location
    Substation location
  Missing information:
    Substation connection
    Physical parameters (line parameter, load, voltage level, transformer size, device parameter)

## Slide 12: Grid impact analysis update
Exelon GIS data and ATEAM study area comparison
  Red area: ATEAM study area
  Green area: available Exelon GIS data
  We choose MD area as our target study area
Test feeder model
  Use available excel files from GIS data
    Check with Exelon engineer about data meaning
    Coding for selecting information from a specific feeder
  Use CYME model from Exelon
    Not sure whether they will provide it
    Once they provide it, we will work on translating CYME file to OpenDSS file

## Slide 13: Grid impact analysis update
Study level
  Feeder level analysis using Exelon data (check with Exelon)
  T&D example with IEEE 8500 nodes system
Economic generic data preparation
  Substation expansion cost
  Charging station building cost (from Joann)
  Charger cost (from Joann)
  Line expansion cost
  Wholesale electricity price
  Utility electricity price (NREL database)
Study scenarios discussion
  Peak day

## Slide 14: Grid impact analysis update
BEG CYME Data
  Received data on Tuesday, roughly went through the data
  304 tables in total, around 100 tables with value
  Which area covered? Different from previous PHI GIS data? GIS data covers DC, part of Maryland, Virginia, New Jersey, Delaware
  We do not have CYME license. Need to figure out how to work with the data
BEG CYME Data Comparison with Data Request
  Distribution feeder data requested are available in the CYME data
  Customer load available in the CYME data
  Need more time to check whether all parameters are complete
  Control logic, DER data, load profile not available from Exelon
  Economic information not provided yet, but can use generic data as substitute

## Slide 15: Grid impact analysis update
Summary of BGE CYME Data
  1758 feeders and 1684 feeder dependencies
  180 sources and 5680 equivalent source
  1002989 nodes, 5003282 intermediate point, 14710 node inter, 1898 head node
  785806 customer load, 207808 load, 5673 equivalent load
  250854 overhead line, 257105 underground line, 207480 transformer, 258660 switch
  5397 shunt capacitor, 80 regulator, 707 load tap changer, 80 auto tap changer
  148264 fuse, 3022 breaker, 4184 recloser, 1685 sectionalizer
  1027156 section, 226510 section UDD, 1344761 section device
  6988 structure, 20620 structure connection
  216882 device UDD, 3434 meter

## Slide 16: Grid impact analysis update
Some questions about BGE CYME Data
  Feeder number and source number not matching. Some feeders with multiple sources.
  Feeder dependencies meaning.
  Node location converted to latitude/longitude: X=474914.384 Y=195182.113
  Technical details about data meaning and correlation among different tables.
CYMNETWORKDEPENDENCIES |  | 
NetworkId1 | NetworkId2 | Child
13003 | CENTER_13KV | 1
13004 | CENTER_13KV | 1

## Slide 17: Grid impact analysis update
Future plan
  Determine study area and study level, feeder level or large scale network
  Need more time to figure out CYME data. Good if we can have technical detail support from Exelon experts.
  Using python to read CYME data and work with data
  Plot node locations to understand where the networks are in the map
  Filter feeder and extract all related information, select a feeder of interest
  Convert CYME data into Gridlabd/OpenDSS format depending on what tools we can find. Might take several steps to finally get OpenDSS model
  Writing codes for converting data to accommodate existing data information
  Validate OpenDSS model power flow
  Repeat for two or three feeders

## Slide 18: Data collection update
PHI Data
BGE Data
Delmarva Data

## Slide 19: overall plan
PHI and BGE Cyme Network
PHI and BGE OpenDSS Network
Typical Feeders
ATEAM Charing Schedule
Power Flow Analysis in Feeder Level
Charging Schedule Mapping and Disaggregation to Feeder Level
Economic Analysis in Feeder Level
T&D Co-simulation
Step 1:Data Collection and Network Modeling
Step 2: ATEAM Coupling
Step 3: Grid Impact Physical, Economic, T&D Analysis

## Slide 20: Data collection and network modeling
Collect Exelon network data: PHI, BGE, Delmarva
Determine data source to use: PHI, BGE data which covers Baltimore and DC to align with ATEAM study area
Collect PHI and BGE data in cyme txt format: we have 2 BGE feeders in cyme txt
Develop multi-source Cyme(txt)-OpenDSS conversion tool
Determine typical feeders in PHI and BGE network
Convert selected feeders to OpenDSS format
Generic Data Collection: cost, electricity prices
No milestone for CEEESA in BP2
Cyme(txt)-OpenDSS Conversion Tool
  Why we need it: to accommodate customized models in analysis, conduct different types of analysis with more flexibility, and to be integrated in T&D co-simulation tool
  Challenges: unclear about physical definition, attributes and how to separate different feeders
  Working on tool development to translate multiple feeders with multiple sources (not supported in current version of the tool)
  Doable, but would take a couple of months
Feeder Selection
  Needs more discussion about which feeders to select as typical feeders in analysis
PHI and BGE Cyme Network
PHI and BGE OpenDSS Network
Typical Feeders
Step 1:Data Collection and Network Modeling

## Slide 21: Ateam coupling
ATEAM Charing Schedule
Charging Schedule Mapping and Disaggregation to Feeder Level
Step 2: ATEAM Coupling
Collect ATEAM results in selected feeder area
Disaggregate ATEAM result to nodes in the feeder level
Model EVCS in the selected feeders with location, capacity, EVSE type, and charging profile
We do not have ATEAM example result now
Node
Line
Substation
EVCS
Impedance

## Slide 22: Grid impact analysis
Power Flow Analysis in Feeder Level
Economic Analysis in Feeder Level
T&D Co-simulation
Step 3: Grid Impact Physical, Economic, T&D Analysis
Power Flow Analysis
  Run power flow on selected feeders with EVCS charging profiles from ATEAM
  Check voltage profiles, network losses, line congestion, transformer overload, overall loading condition, peak load in the network
  Conduct time series power flow with different load profiles, different EV charging profiles and different EV penetration level
Chart: Node
| 0 | 1 | 2 | 3 | 4 | 5
Vbefore | 1.01 | 1 | 0.99 | 0.98 | 0.97 | 0.95
Vafter | 1.01 | 0.99 | 0.98 | 0.96 | 0.93 | 0.9
Economic Analysis
  Evaluate revenue and operational cost of smart charging management and grid service provision profiles
  Assess grid upgrade needs, cost and benefits based on grid and EVSE expansion scenarios
T&D Co-simulation Analysis
  Using IEEE standard transmission network and BGE distribution feeders in co-simulation platform
Connected to

## Slide 23: Data collection and network modeling
SOURCE_7773
SOURCE_7732
Cyme(txt)-OpenDSS Conversion Tool Progress
  New Capabilities
    Grouping sections, nodes, devices by feeders
    Create separate models for each feeder and convert to OpenDSS feeder by feeder
    Converted multiple feeders with multiple sources from Cyme to OpenDSS at one time
  Outcomes for converted two feeders
    Feeder 7732 with 871 nodes, Feeder 7773 with 607 nodes

## Slide 24: Data collection and network modeling
Cyme(txt)-OpenDSS Conversion Tool Progress
  Issues in the converted two feeders
    Series lines with duplicate names
    Node name with “.” does not satisfy OpenDSS name rules
    Wrong phase connection for load: 2-phase load on one phase, 6-phase load
    Networks contain loops: check whether it is due to normal-open switches
    Networks contain duplicate line: check whether it is due to normal-open switches
  Next Step
    Check three/two/single phase line/transformer/load information
    Solve above issues in conversion tool and check for any other issues in OpenDSS file
    Plot these two feeders on map
      Need to check with Exelon which crs they are using for coordinates
    Check power flow results with BGE
      Need to ask BGE to provide power flow results for these two feeders
    Add capability for converting multiple substation network

## Slide 25: Data collection and network modeling
Feeder Selection Criteria
  Align in the ATEAM study area (see attached map). Maybe choose some from the PHI network and some from the BGE network. The map is also available here: https://www.google.com/maps/d/u/0/edit?mid=1v6F3lLqyTdigKkP04ogTr_p4uA5iKYY&usp=sharing
  Choose feeders with different voltage levels
  Choose feeders in different areas type (for example, choose some from urban areas, semi-urban areas, or rural areas)
  Choose feeders with different load types (for example, choose some mainly with commercial load, some mainly with residential load or industrial load)
  Choose some feeders in a heavy populated area and some from not so heavy populated area
  Choose some feeders with large service areas and some with small service areas
  Choose feeders with and without devices (regulator, switch, recloser, transformer)
  Any feeders that Exelon is interested in, regardless of the above criteria